## Instructions
I&E Systems Pty Ltd
DISCLAIMER: Whilst every effort has been made to ensure the accuracy of the information contained in this spreadsheet neither “The 61508 Association” nor its members will assume any liability for any use made thereof.
A detailed explanation of the failure probability calculation model is available at:
https://www.iesystems.com.au/The-MooN-SIF-model.pdf
1 | Start with failure modes and effects analysis
Prepare a failure modes and effects analysis (FMEA) sheet for each distinct type of subsystem. Copy the example FMEA sheets.
Refer to IEC 60812 for guidance on FMEA.
The primary purpose of the FMEA is to faciltate subsystem design so that: 1. Dangerous failures may be prevented by design 2. Unpreventable dangerous failures may be detected by continuous diagnostic functions 3. Proof test and inspection may be designed to reveal the unpreventable dangerous failures that cannot be detected by diagnostics
FMEA is always necessary as the first step. Failiure modes and effects always depend on the specific application of devices and on the overall design of each subsystem.
FMEA published in device safety manuals or in exida SERH may be used as references but are not sufficient on their own. Failure rates and failure effects depend on each specific application.
Each susbsystem FMEA should contain all of the subsystem components. For instance, FMEA for a sensor subsystem should include the process interface, the process connection, the sensor, the transmitter, the signal wiring, signal conversion elements (such as isolating barriers) and the logic solver input channel.
Example FMEA sheets are included for a sensor, logic solver and final element.
Enter information into cells shaded this colour
Use dropdown lists in the darker cells
Grey shaded cells show calculation results or references to other cells
Do not use spaces in the FMEA sheet names. The lookup reference functions will not work if the sheet names include spaces.
The logic solver FMEA may be simplified and refer to consolidated data from the device safety manual. Sheet FMEA_2 shows an example. Logic solvers do not usually make a significant contribution to the overall safety function failure probability.
All failure rates are variable in practice. Element failure rate estimates should be expected to vary by at least 0.3x to 3x around the long term averages. Refer to references 3, 4, 5, 6 and 7 below for information on failure rate variability.
Failure rates vary widely because at least 97% of failures are at least partially systematic. Failure rates depend environmental factors and on the effectiveness of equipment maintenance practices.
Refer to SILsafedata.com (reference 10 below) for the typical ranges of failure rates that can be achieved in practice. Beware that some equipment certificates show failure rates that are 30 to 50 times lower than these ranges because they specifically exclude systematic failures - but those are the failures that matter most.
FMEA does not need to be precise. Break each subsytem down into its main component parts. A typical FMEA for the purpose of PFD calculations does not need more than about 30 rows. It may have fewer than 10 rows.
There is no such thing as a 'correct' or 'true' value of failure rate. Initial estimates for failure rates on individual rows of FMEA can be derived from the typical values of overall failure rate taken from reference sources. For example, a sensor might be expected to have an overall failure rate of around 3000 FITS. If 10 individual failure modes are identified, then the average failure rate of each mode would have to be around 300 FITS. One or two components might be estimated to fail more frequently, so they might be assigned 1000 FITS. Other components that are less likely to fail would be assigned 30 FITS or 100 FITS. The point of the exercise is to identify the dangerous failure modes that can be expected and to identify ways of avoiding, controlling, preventing or detecting faults before they result in failure.
Understand that many failure rates will depend on the decisions made in design, installation and maintenance. For example, loose or corroded wiring connections may lead to a dangerous failure through increased impedance in a sensor loop. Loose connections can be avoided by using high integrity terminals (such as Ex n or Ex e designs). Corrosion in wiring connections can be minimised by using materials suitable for the environment and by protecting termination boxes from weather. Tracking between terminals can be minimised by using Ex e designs and again by providing appropriate ingress protection and weather protection. The average rate of failure due to high impedance connections could be anywhere between 3 FITS and 300 FITS.
Determine whether each failure mode is safe or dangerous in the context of the specific application. Safe failures increase the probability that the safety function will put the equipment into a safe state. Dangerous failures increase the probability that the safety function will fail to achieve or maintain a safe state.
Identify diagnostic functions that have already been included in the design or that can be added. Note that a diagnostic function that is claimed to have reliability better than 90% would have to be subject to appropriate techniques and measures to prevent failure.
Identify which faults and failures can be revealed by proof test and inspection. Similarly, inspection and test could be claimed to have coverage better than 90%, but would have to be subject to appropriate techniques and measures. Some form of independent checking or review would usually be needed to achieve better than 99% coverage.
2 | Assemble each safety function using a combination of subsystems
Make a copy of the safety function analysis sheet SF_1 to define a safety function. Prepare separate sheets to define each unique safety function pattern.
The safety function analysis sheet contains sections to define each of the three subsystems: Sensor, Logic solver and Final elements
For each subsytem enter the name of the FMEA sheet prepared for that subsystem. Reference error messages will be shown if the name entered is not a valid sheet name.
The same FMEA can be referenced by several different safety functions. The SF worksheet looks up failure rates from the referenced FMEA sheets.
The logic solver subsystem does not usually conribute more then a few percent to the overall failure probability. The logic solver section on the safety function sheet can be simplified by not using an FMEA sheet. The contribution to PFD could be overwritten with fixed nominal values taken from the safety manual.
Define the variable parameters in each subsystem section on the SF worksheet: M out of N voting architecture, the test intervals T1 and T2, the MTTR, MRT and βint factor.
Refer to IEC 61508 part 6 or to the SINTEF PDS Method handbook for guidance in estimating the common cause failure fraction βint.
Use 10% as the default value for the βint factor in sensor and final element subsystems if it has not been calculated specifically.
The calculations including β scaling factors for MooN architectures.
The estimate for spurious trip rate and MTTFS (mean time to fail safe) only includes the rate of undetected safe faulures, λSU. The assumption is that a diagnostic alarm will be raised for detected faults (λSD and λDD) rather than automatically tripping to the safe state.
Logic solver 1oo2D architecture calculations are not supported. Use 2oo3 as a close approximation. The PFD and spurious trip rate of 1oo2D is similar to 2oo3. The differences are negligible given the uncertainty in failure rates.
3 | Evidence of suitability
The FMEA sheets include space to record evidence of suitability. Include a reference either to a safety manual or to a prior use analysis report.
The safety function analysis sheet contains cells for each subsystem with dropdown boxes to record Selection criteria - suitability for use. Select the appropriate value from the dropdown list.
The architectural constraints analysis (hardware fault tolerance) can only be completed if there is evidence that the selected devices are suitable for the intended use.
The safety function analysis sheet contains cells to record systematic capability. Systematic capability only applies to devices that are claimed to comply to IEC 61508. Select 0 from the dropdown options if systematic capability is not applicable, the cell is formatted to show N/A when 0 is selected. Systematic capability does not apply for devices selected on the basis of prior use or on the basis of compliance to other appropriate standards.
4 | Design margins
The SIL determination guidelines in IEC 61508-5 and IEC 61511-3 explain that risk reduction targets should be set to achieve a residual risk that is lower than the tolerable risk. It is good practice to allow some design margin in safety functions so that its estimated risk reduction factor is greater than the target risk reduction allocated to the safety system.
The usual practice is to design safety functions using failure rates with a 70% statistical confidence level or 70% certainty level. Note that statistical confidence levels only apply to measurements of paramaters that have a single true value. Confidence levels may be applied only to the purely random proportion of failure rates for individual electronic components. The OREDA datasets use certainty levels rather than confidence levels because it is clear that different users measure different values of failure rate. In general certainty levels should be used instead of confidence levels. A certainty level of 70% means that there is a 70% chance that the failure rate can be achieved in operation. There is a 30% chance that the failure rate will be worse than the chosen value.
The failure rates reported in exida SERH are generally consistent with the 70 percentile values reported in the OREDA datasets. The worst-case performance reported in OREDA is typically a factor of 3 or 4 higher than the 70% levels. Bukowski, J.V. and Stewart, L. (Reference 7) reported a similar factor in worst-case performance on sites where maintenance activities were not completed promptly and effectively.
The safety function analysis sheet includes a summary section that reports the expected range of variation in safety function performance. The default setting for the uncertainty range is one order of magnitude.
System designers should establish if the risk target allocated to the safety system already includes some margin with respect to tolerable risk. If a margin is not included in the target then it is good practice to design safety functions so that the estimated risk reduction is 2 or 3 times higher than the allocated target. A margin of 3 should be enough to compensate for performance that is worse than the 70% benchmark. If the estimated performance exactly meets the allocated target then there is about a 30% chance that the performance will be worse than the target value. This may be acceptable if the residual risk is as low as reaonably practicable (ALARP), i.e. further risk reduction is impracticable or the cost of further risk reduction is grossly disproportionate with respect to the benefit.
5 | Staggered testing
The option of staggered testing can be selected for sensors and final elements. The 'Regular test period T1' is then the maximum interval between test and inspection on any one device. The time interval between tests on N different channels is T1/N. For instance with 2 channels and T1 = 1 year, the tests on individual devices are at 6 month intervals. With 3 channels the individual tests would be at 4 month intervals. The calculation method is described in references 11 and 15.
Users should be aware that extending test intervals of actuated valves beyond one year can be expected to dramatically increase the failure rates. Valves need to be moved at least once or twice a year to prevent them from sticking. Staggered testing only makes sense if the test interval for each individual valve is no more than 1 year. Staggered testing should not be used to justiy extending T1 to greater than 1 year.
Staggered testing is usually practicable for sensors, because they can be bypassed for testing on-line during normal operation. There is no point in staggering testing of final elements in any 1oo2 arrangement because if one element is tripped then the process will be oput into the safe state and normal operation interrupted. We might as well trip the other element at the same opportunity. Staggered testing is beneficial for final element architectures such as 2oo3 (like the Woodward QuickTrip valves) or 2oo3 x (1oo2), i.e. 3 parallel branches of 1oo2 valves.
The benefit of staggered testing is that it enables common cause failuresto be revealed at intervals of T1/N rather than T1. The model assumes that failures found in individual devices are analysed. Other similar devices should be immediately inspected and/or tested if the causes of failure are expected to affect other similar devices in a similar way.
6 | Make a summary sheet
The safety function sheet names can be used to summarise results on the Summary sheet. Make sure that there are no spaces in the sheet names. The 'INDIRECT' referencing function does not work if the sheet names contain spaces.
This workbook is intended to include no more than 10 or 20 different safety function sheets. Consider using multiple workbooks for larger applications so that the file is not too cumbersome.
References
1 | IEC 60812 Analysis techniques for system reliability – Procedure for failure mode and effects analysis (FMEA)
2 | IEC 61508 Functional safety of electrical/electronic/programmable electronic safety-related systems
3 | IEC 61709 Electronic components – Reliability – Reference conditions for failure rates and stress models for conversion
4 | Smith, D. J. ‘Reliability, Maintainability and Risk’, 9th Ed. Butterworth Heinemann. 2017
5 | OREDA ‘Offshore Reliability Data Handbook’ Volume 1, 5th Ed. SINTEF. 2009
6 | OREDA ‘Offshore and Onshore Reliability Data Handbook’ Volume 1, 6th Ed. SINTEF. 2015
7 | Bukowski, J.V. and Stewart, L. ‘Quantifying the Impacts of Human Factors on Functional Safety’ exida. Presented at the American Institute of Chemical Engineers’ 12th Global Congress on Process Safety, Houston, Texas. 2016
8 | exida Safety Equipment Reliability Handbook (‘SERH’), 3rd Ed. 2007
9 | exida Safety Equipment Reliability Handbook (‘SERH’), 4th Ed. 2015
10 | SILsafedata.com
11 | SINTEF Reliability Prediction Method for Safety Instrumented Systems PDS Method Handbook. 2013
12 | SINTEF Reliability Prediction Method for Safety Instrumented Systems PDS Data Handbook. 2021
13 | Florent Brissaud, Anne Barros, Christophe Bérenguer. ‘Probability of Failure of Safety-Critical Systems Subject to Partial Tests. Reliability and Maintainability Symposium, RAMS 2010, San Jose (referenced in Cornell University Library, < arXiv:1007.5448 >).
14 | ISA-TR84.00.02-2022 Part 1 Safety Integrity Level (SIL) Verification of Safety Instrumented Functions
15 | The 61508 Association, T6A042 Development Paper – Effects of Proof Testing Version 0.2, February 2022
16 | Jahanian, Hamid. ‘Generalizing PFD formulas of IEC 61508 for KooN configurations’. ISA Transactions 56 pp 168-174. 2015
Acknowledgement
The generalised MooN equation used in this workbook is based on equations published in references 4, 11, 13 and 16

## About
MoonSIF calculation tool
Version | 0.4. | Released | 2024-07-01
Created and licensed by I&E Systems Pty Ltd with support from The 61508 Association
Author | Mirek Generowicz
Contributors | Ray Martin (for the 61508 Association)
This work is released under a Creative Commons BY-SA Licence.
https://creativecommons.org/licenses/by-sa/4.0/legalcode
Attribution — You must give appropriate credit, provide a link to the license, and indicate if changes were made. You may do so in any reasonable manner, but not in any way that suggests the licensor endorses you or your use.
ShareAlike — If you remix, transform, or build upon the material, you must distribute your contributions under the same license as the original.
You are free to:
Share — copy and redistribute the material in any medium or format
Adapt — remix, transform, and build upon the material for any purpose, even commercially.
The licensor cannot revoke these freedoms as long as you follow the license terms.
<a rel="license" href="http://creativecommons.org/licenses/by-sa/4.0/"><img alt="Creative Commons License" style="border-width:0" src="https://i.creativecommons.org/l/by-sa/4.0/88x31.png" /></a><br /><span xmlns:dct="http://purl.org/dc/terms/" property="dct:title">MoonSIF</span> by <a xmlns:cc="http://creativecommons.org/ns#" href="www.iesystems.com.au" property="cc:attributionName" rel="cc:attributionURL">I&E Systems Pty Ltd</a> is licensed under a <a rel="license" href="http://creativecommons.org/licenses/by-sa/4.0/">Creative Commons Attribution-ShareAlike 4.0 International License</a>.<br />Based on a work at <a xmlns:dct="http://purl.org/dc/terms/" href="https://www.iesystems.com.au/publications/" rel="dct:source">https://www.iesystems.com.au/publications/</a>.
Version | Date | Description
0.0. | 2023-05-30 | First release for general use
0.1. | 2023-06-21 | Added correction factor for synchronsed testing into the 'average before' model for low demand mode, deleted the expanded model
0.2. | 2023-08-02 | Corrected range name reference for RRF_target on summary sheet
0.3. | 2023-11-29 | Corrected link to explanatory notes to'.pdf' instead of '.docx'
0.4. | 2024-07-01 | Updated link to explanatory notes

## Summary
I&E Systems Pty Ltd
FOR EXAMPLE ONLY. This summary uses the SF sheet names to index named ranges on the individual sheets. Use the sheet name as an index. The reference functions will not work with sheet names that contain spaces. Copy the example row.
Sheet index | SF ID: | Description | SIL Target | SIL Achieved | HFT Limit | RRF Target | RRF Achieved | RRF Margin | MTTFS (years) | Remarks
SF_1_LD | SF 001 | Example safety function description: Flare knock-out drum high level trip | 2 | 2 | 3 | 300 | 600 | 2 | 60

## SF_1_LD
I&E Systems Pty Ltd
Make a separate copy of this sheet to define each different type of safety function | [10 empty] | Low demand mode
Enter information on this sheet only in the cells shaded: | [7 empty] | Grey shaded cells show information linked from calculation sheets
Darker shaded cells have data validation and dropdown menus:
Safety function ID: |  |  |  | SF 001 |  |  |  | SIL target: | 2 |  |  |  | RRF target: | 300
Function description
Example safety function description: Flare knock-out drum high level trip
Sensor subsystem
Sensor equipment description
Describe the sensor subsystem here
| FMEA sheet reference |  |  | FMEA_1 |  |  |  | Eqpt ID | PZHH01
Manufacturer and model
Generic 4-20mA pressure transmitter with impulse line connection
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | IEC 61508 safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 1
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 1 | out of | 2 |  |  | Fault tolerance: |  | 1
| Route 1H SIL limit: |  | 2 |  | Route 1H factors: |  | Type B | SFF | 80.98% | 12 |  | Chosen HFT Route: |  | IEC 61511
| Route 2H SIL limit: |  | 3 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 3
| IEC 61511 SIL limit: |  | 3 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Regular test period T1 (y) |  | 1 | T1 test coverage | 97.18% |  | MRT (days) | 3 |  | βint | 10% | Correction factors for MooN voting
| Staggered testing: |  | 0 |  |  |  | MTTR (days) | 3 |  | βDint | 10% | are applied in the calculations below
| Full test period T2 (y) |  | 10
Logic solver subsystem
Logic solver equipment description
| FMEA sheet reference |  |  | FMEA_2 |  |  |  | Eqpt ID | Solver1
| Manufacturer and model |  |  | from the FMEA sheet
Generic 2oo3
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | IEC 61508 safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 3
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 2 | out of | 3 |  |  | Fault tolerance: |  | 1
| Route 1H SIL limit: |  | 3 |  | Route 1H factors: |  | Type B | SFF | 95.45% | 13 |  | Chosen HFT Route: |  | Route 1H
| Route 2H SIL limit: |  | 3 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 3
| IEC 61511 SIL limit: |  | 3 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Regular test period T1 (y) |  | 1 | T1 test coverage | 100% |  | MRT (days) | 3 |  | βint | 5% | Correction factors for MooN voting
| Full test period T2 (y) |  | 10 |  |  |  | MTTR (days) | 3 |  | βDint | 5% | are applied in the calculations below
Final element subsystem
Final element equipment description
| FMEA sheet reference |  |  | FMEA_3 |  |  |  | Eqpt ID | FE01
Manufacturer and model
Generic data
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | Other safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 0
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 1 | out of | 2 |  |  | Fault tolerance: |  | 1
| Route 1H SIL limit: |  | 2 |  | Route 1H factors: |  | Type A | SFF | 20.69% | 1 |  | Chosen HFT Route: |  | IEC 61511
| Route 2H SIL limit: |  | 3 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 3
| IEC 61511 SIL limit: |  | 3 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Regular test period T1 (y) |  | 1 | T1 test coverage | 97.83% |  | MRT (days) | 3 |  | βint | 10% | Correction factors for MooN voting
| Staggered testing: |  | 0 |  |  |  | MTTR (days) | 3 |  | βDint | 10% | are applied in the calculations below
| Full test period T2 (y) |  | 10
Safety function ID: |  |  |  | SF 001 |  |  |  | SIL target: | 2 |  |  |  | RRF target: | 300
[8 empty] | SIL achieved by RRF: | 2 |  |  |  | RRF achieved: | 600
[8 empty] | SF overall HFT limit: | 3
Reliability block diagram and safety function performance summary
|  |  | PZHH01 |  | Solver1 |  | FE01
|  |  | 1oo2 |  | 2oo3 |  | 1oo2
PFDAVG |  |  | 0.00023 |  | 2.2e-05 |  | 0.0014 |  |  |  | SF Total PFDAVG |  | 0.002
Spurious trip rate (pa) |  |  | 0.0080592 |  | 3.2859e-05 |  | 0.0080592 |  |  |  | SF spurious trip rate |  | 0.02 | pa
Evidence of suitability |  |  | IEC 61508 safety manual |  | IEC 61508 safety manual |  | Other safety manual
HFT Limit |  |  | 3 |  | 3 |  | 3
Sytematic capability |  |  | 1 |  | 3 |  | 0
Uncertainty range: |  |  | 1 | orders of magnitude
Rounding totals to: |  |  | 1 | significant figures
|  |  | RRF Achieved |  | MTTFS (years)
Low range uncertainty boundary |  |  | 200 |  | 20
Estimated average values |  |  | 600 |  | 60
Upper range uncertainty boundary |  |  | 2000 |  | 200 |  |  | Chart data |  |  | uncertainty factor | 3.1623
[8 empty] | low | average | high |  | Target RRF | Estimated RRF
[8 empty] | 200 | 600 | 2000 |  | 300 | 600
[8 empty] | 200 | 600 | 2000 |  | 300 | 600
[6 empty] | Sensor | 11.5%
[6 empty] | Logic | 1.1%
[6 empty] | Final element | 70%
MooN model, with the average PFD of 1oo1 raised to the (N-M+1)th power
Synchronised testing:
[39 empty] | Staggered tests reduce T for the CCF terms, assuming that identification of CCF is included in analysis of all failures |  |  |  | This simple rule of thumb is valid if Beta is in the range 5% to 10%
Staggered testing:
Subsystem PFD Estimates | [28 empty] | Spurious trip rate:
Rounding to | 2 | significant figures
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45
[7 empty] | Regular periodic test | Full test |  |  |  |  | β for 1oo2 architecture |  | β for MooN architecture | [19 empty] | The colour shading highlights the largest term | [7 empty] | Simple rule of thumb
Subsystem Index | PFDAVG | MTTFS (years) | FMEA sheet name | M | N | Voting | T1 years | T2 years | MTTR days | MRT days | MTTR years | MRT years | β | βD | MooN β | MooN βD | λdu FITS | λdu pa | λdd FITS | λdd pa | DC | SFF | λdn FITS | λdn pa | PTC | λsu FITS | λsu pa |  | STR β | Voted STR term | CCF STR term | STR |  |  | voted T1+T2+MTTR term, average before | CCF T1 term | CCF T2 term | CCF λDD term | Staggered? | CCF T/N | MooN model Total PFDAVG |  | PFDAVG | % lower than the 'PFDMooN' model
PZHH01 | 0.00023 | 120 | FMEA_1 | 1 | 2 | 1oo2 | 1 | 10 | 3 | 3 | 0.0082192 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 390 | 0.0034164 | 1200 | 0.010512 | 75.47% | 80.98% | 11 | 9.636e-05 | 97.18% | 460 | 0.0040296 | 2 | 0 | 0.0080592 | 0 | 0.0080592 |  | 1 | 4.0216e-06 | 0.000166 | 4.818e-05 | 8.64e-06 | 0 | 1 | 0.00022818 |  | 0.00022776 | 0.1859%
Solver1 | 2.2e-05 | 30000 | FMEA_2 | 2 | 3 | 2oo3 | 1 | 10 | 3 | 3 | 0.0082192 | 0.0082192 | 0.05 | 0.05 | 0.075 | 0.075 | 50 | 0.000438 | 1000 | 0.00876 | 95.24% | 95.45% | 0 | 0 | 100% | 50 | 0.000438 | 6 | 1.5 | 9.4608e-09 | 3.285e-05 | 3.2859e-05 |  | 3 | 2.1737e-07 | 1.6425e-05 | 0 | 5.4e-06 | FALSE | 1 | 2.2115e-05 |  | 2.19e-05 | 0.9714%
FE01 | 0.0014 | 120 | FMEA_3 | 1 | 2 | 1oo2 | 1 | 10 | 3 | 3 | 0.0082192 | 0.0082192 | 0.1 | 0.1 | 0.1 | 0.1 | 2300 | 0.020148 | 140 | 0.0012264 | 5.738% | 20.69% | 50 | 0.000438 | 97.83% | 460 | 0.0040296 | 2 | 0 | 0.0080592 | 0 | 0.0080592 |  | 1 | 0.00011771 | 0.0009855 | 0.000219 | 1.008e-06 | 0 | 1 | 0.0013625 |  | 0.0013432 | 1.414%
Insert additional rows if needed above this row to maintain the range name references, and copy calculations into the new rows as required
STR = [N! / (N-M)! . (λSU )M . MTTR(M-1) ] + β . (λSU )

## SF_2_HD
I&E Systems Pty Ltd
Make a separate copy of this sheet to define each different type of safety function | [10 empty] | High demand mode
Enter information on this sheet only in the cells shaded: | [7 empty] | Grey shaded cells show information linked from calculation sheets
Darker shaded cells have data validation and dropdown menus:
Safety function ID: |  |  |  | SF 002 |  |  |  | SIL target: | 2 |  |  | PFH target: | 1e-06 | /h
Function description
Example safety function description: Flare knock-out drum high level trip
Sensor subsystem
Sensor equipment description
Describe the sensor subsystem here
| FMEA sheet reference |  |  | FMEA_1 |  |  |  | Eqpt ID | PZHH01
Manufacturer and model
Generic 4-20mA pressure transmitter with impulse line connection
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | IEC 61508 safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 1
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 1 | out of | 1 |  |  | Fault tolerance: |  | 0
| Route 1H SIL limit: |  | 1 |  | Route 1H factors: |  | Type B | SFF | 80.98% | 12 |  | Chosen HFT Route: |  | IEC 61511
| Route 2H SIL limit: |  | 2 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 2
| IEC 61511 SIL limit: |  | 2 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Test period T1 (y) |  | 1 |  |  |  | MRT (days) | 3 |  | βint | 10% | Correction factors for MooN voting
[7 empty] | MTTR (days) | 3 |  | βDint | 10% | are applied in the calculations below
Logic solver subsystem
Logic solver equipment description
| FMEA sheet reference |  |  | FMEA_2 |  |  |  | Eqpt ID | Solver1
| Manufacturer and model |  |  | from the FMEA sheet
Generic 2oo3
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | IEC 61508 safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 3
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 1 | out of | 3 |  |  | Fault tolerance: |  | 2
| Route 1H SIL limit: |  | 4 |  | Route 1H factors: |  | Type B | SFF | 95.45% | 13 |  | Chosen HFT Route: |  | Route 1H
| Route 2H SIL limit: |  | 4 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 4
| IEC 61511 SIL limit: |  | 4 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Test period T1 (y) |  | 1 |  |  |  | MRT (days) | 3 |  | βint | 5% | Correction factors for MooN voting
[7 empty] | MTTR (days) | 3 |  | βDint | 5% | are applied in the calculations below
Final element subsystem
Final element equipment description
| FMEA sheet reference |  |  | FMEA_3 |  |  |  | Eqpt ID | FE01
Manufacturer and model
Generic data
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | Other safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 0
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 4 | out of | 7 |  |  | Fault tolerance: |  | 3
| Route 1H SIL limit: |  | 4 |  | Route 1H factors: |  | Type A | SFF | 20.69% | 1 |  | Chosen HFT Route: |  | IEC 61511
| Route 2H SIL limit: |  | 4 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 4
| IEC 61511 SIL limit: |  | 4 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Test period T1 (y) |  | 1 |  |  |  | MRT (days) | 3 |  | βint | 10% | Correction factors for MooN voting
[7 empty] | MTTR (days) | 3 |  | βDint | 10% | are applied in the calculations below
Safety function ID: |  |  |  | SF 002 |  |  |  | SIL target: | 2 |  |  | PFH target: | 1e-06 | /h
[8 empty] | SIL achieved by PFH: | 2 |  |  | PFH achieved: | 9e-07 | /h
[8 empty] | SF overall HFT limit: | 2
Reliability block diagram and safety function performance summary | [10 empty] | High demand mode
This model assumes that the safety function acts to put equipment into the safe state in response to detected failures in architectures with no fault tolerance (M=N)
|  |  | PZHH01 |  | Solver1 |  | FE01
|  |  | 1oo1 |  | 1oo3 |  | 4oo7
PFH |  |  | 3.9e-07 |  | 1.3e-09 |  | 4.6e-07 |  |  |  | SF Total PFH |  | 9e-07 | /h
Spurious trip rate (pa) |  |  | 0.0040296 |  | 0.001314 |  | 0.00080592 |  |  |  | SF spurious trip rate |  | 0.006 | pa
Evidence of suitability |  |  | IEC 61508 safety manual |  | IEC 61508 safety manual |  | Other safety manual
HFT Limit |  |  | 2 |  | 4 |  | 4
Sytematic capability |  |  | 1 |  | 3 |  | 0
Uncertainty range: |  |  | 1 | orders of magnitude | [7 empty] | RRF target: | N/A
Rounding totals to: |  |  | 1 | significant figures | [7 empty] | RRF achieved: | N/A
|  |  | PFH Achieved |  | MTTFS (years)
Low range uncertainty boundary |  |  | 3e-07 |  | 60
Estimated average values |  |  | 9e-07 |  | 200
Upper range uncertainty boundary |  |  | 3e-06 |  | 600 |  |  | Chart data |  |  | uncertainty factor | 3.1623
[8 empty] | low | average | high |  | Target PFH | Estimated PFH
[8 empty] | 3e-07 | 9e-07 | 3e-06 |  | 1e-06 | 9e-07
[8 empty] | 3e-07 | 9e-07 | 3e-06 |  | 1e-06 | 9e-07
[6 empty] | Sensor | 43.33%
[6 empty] | Logic | 0.1444%
[6 empty] | Final element | 51.11%
Subsystem PFH Estimates
Spurious trip rate:
Rounding to | 2 | significant figures
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
[13 empty] | β for 1oo2 architecture |  | β for MooN architecture
Subsystem Index | PFH | MTTFS (years) | FMEA sheet name | M | N | Voting | T1 years |  | MTTR days | MRT days | MTTR hours | MRT hours | β | βD | MooN β | MooN βD | λdu FITS | λdu per hour | λdd FITS | λdd per hour | DC | SFF |  | λd per hour |  | λsu FITS | λsu per hour |  | MDT1oo2 | CCF term | PFHDMooN | PFH |  |  | STR β | Voted STR term | CCF STR term | STR
PZHH01 | 3.9e-07 | 250 | FMEA_1 | 1 | 1 | 1oo1 | 1 |  | 3 | 3 | 72 | 72 | 0.1 | 0.1 | 0 | 0 | 390 | 3.9e-07 | 1200 | 1.2e-06 | 75.47% | 80.98% |  | 1.59e-06 |  | 460 | 4.6e-07 | 1 | 0.0018227 | 0 | 3.9e-07 | 3.9e-07 |  | 1 | 0 | 0.0040296 | 0 | 0.0040296
Solver1 | 1.3e-09 | 760 | FMEA_2 | 1 | 3 | 1oo3 | 1 |  | 3 | 3 | 72 | 72 | 0.05 | 0.05 | 0.025 | 0.025 | 50 | 5e-08 | 1000 | 1e-06 | 95.24% | 95.45% |  | 1.05e-06 |  | 50 | 5e-08 | 6 | 0.00028723 | 1.25e-09 | 2.4751e-14 | 1.25e-09 |  | 3 | 0 | 0.001314 | 0 | 0.001314
FE01 | 4.6e-07 | 1200 | FMEA_3 | 4 | 7 | 4oo7 | 1 |  | 3 | 3 | 72 | 72 | 0.1 | 0.1 | 0.2 | 0.2 | 2300 | 2.3e-06 | 140 | 1.4e-07 | 5.738% | 20.69% |  | 2.44e-06 |  | 460 | 4.6e-07 | 840 | 0.0081997 | 4.6e-07 | 1.0651e-09 | 4.6107e-07 |  | 840 | 2 | 1.2297e-13 | 0.00080592 | 0.00080592
Insert additional rows if needed above this row to maintain the range name references, and copy calculations into the new rows as required
STR = [N! / (N-M)! . (λSU )M . MTTR(M-1) ] + β . (λSU )

## SF_3_CM
I&E Systems Pty Ltd
Make a separate copy of this sheet to define each different type of safety function | [10 empty] | Continuous mode
Enter information on this sheet only in the cells shaded: | [7 empty] | Grey shaded cells show information linked from calculation sheets
Darker shaded cells have data validation and dropdown menus:
Safety function ID: |  |  |  | SF 003 |  |  |  | SIL target: | 2 |  |  | PFH target: | 1e-06 | /h
Function description
Example safety function description: Flare knock-out drum high level trip
Sensor subsystem
Sensor equipment description
Describe the sensor subsystem here
| FMEA sheet reference |  |  | FMEA_1 |  |  |  | Eqpt ID | PZHH01
Manufacturer and model
Generic 4-20mA pressure transmitter with impulse line connection
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | IEC 61508 safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 1
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 1 | out of | 3 |  |  | Fault tolerance: |  | 2
| Route 1H SIL limit: |  | 3 |  | Route 1H factors: |  | Type B | SFF | 80.98% | 12 |  | Chosen HFT Route: |  | IEC 61511
| Route 2H SIL limit: |  | 4 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 4
| IEC 61511 SIL limit: |  | 4 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Test period T1 (y) |  | 1 |  |  |  | MRT (days) | 3 |  | βint | 10% | Correction factors for MooN voting
[7 empty] | MTTR (days) | 3 |  | βDint | 10% | are applied in the calculations below
Logic solver subsystem
Logic solver equipment description
| FMEA sheet reference |  |  | FMEA_2 |  |  |  | Eqpt ID | Solver1
| Manufacturer and model |  |  | from the FMEA sheet
Generic 2oo3
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | IEC 61508 safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 3
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 2 | out of | 3 |  |  | Fault tolerance: |  | 1
| Route 1H SIL limit: |  | 3 |  | Route 1H factors: |  | Type B | SFF | 95.45% | 13 |  | Chosen HFT Route: |  | Route 1H
| Route 2H SIL limit: |  | 3 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 3
| IEC 61511 SIL limit: |  | 3 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Test period T1 (y) |  | 1 |  |  |  | MRT (days) | 3 |  | βint | 5% | Correction factors for MooN voting
[7 empty] | MTTR (days) | 3 |  | βDint | 5% | are applied in the calculations below
Final element subsystem
Final element equipment description
| FMEA sheet reference |  |  | FMEA_3 |  |  |  | Eqpt ID | FE01
Manufacturer and model
Generic data
Reliability data sources used
Quote references sources here
| Selection criteria - suitability for use |  |  |  | Other safety manual |  |  |  |  | Systematic capability (if IEC 61508 compliant) |  |  |  | 0
Refer to either a safety manual or to a prior use analysis report
Architectural constraints (subject to evidence of suitability)
| Voting architecture |  | 2 | out of | 3 |  |  | Fault tolerance: |  | 1
| Route 1H SIL limit: |  | 2 |  | Route 1H factors: |  | Type A | SFF | 20.69% | 1 |  | Chosen HFT Route: |  | IEC 61511
| Route 2H SIL limit: |  | 3 |  | For Route 2H confirm that reliability data with 90% confidence level has been used | [8 empty] | 3
| IEC 61511 SIL limit: |  | 3 |  | IEC 61511 HFT method requires credible and traceable reliability data
| Test period T1 (y) |  | 1 |  |  |  | MRT (days) | 3 |  | βint | 10% | Correction factors for MooN voting
[7 empty] | MTTR (days) | 3 |  | βDint | 10% | are applied in the calculations below
Safety function ID: |  |  |  | SF 003 |  |  |  | SIL target: | 2 |  |  | PFH target: | 1e-06 | /h
[8 empty] | SIL achieved by PFH: | 2 |  |  | PFH achieved: | 6e-07 | /h
[8 empty] | SF overall HFT limit: | 3
Reliability block diagram and safety function performance summary | [10 empty] | Continuous mode
|  |  | PZHH01 |  | Solver1 |  | FE01
|  |  | 1oo3 |  | 2oo3 |  | 2oo3
PFH |  |  | 8e-08 |  | 7.9e-08 |  | 4.9e-07 |  |  |  | SF Total PFH |  | 6e-07 | /h
Evidence of suitability |  |  | IEC 61508 safety manual |  | IEC 61508 safety manual |  | Other safety manual
HFT Limit |  |  | 4 |  | 3 |  | 3
Sytematic capability |  |  | 1 |  | 3 |  | 0
Uncertainty range: |  |  | 1 | orders of magnitude | [7 empty] | RRF target: | N/A
Rounding totals to: |  |  | 1 | significant figures | [7 empty] | RRF achieved: | N/A
PFH Achieved
Low range uncertainty boundary |  |  | 2e-07
Estimated average values |  |  | 6e-07
Upper range uncertainty boundary |  |  | 2e-06 |  |  |  |  | Chart data |  |  | uncertainty factor | 3.1623
[8 empty] | low | average | high |  | Target PFH | Estimated PFH
[8 empty] | 2e-07 | 6e-07 | 2e-06 |  | 1e-06 | 6e-07
[8 empty] | 2e-07 | 6e-07 | 2e-06 |  | 1e-06 | 6e-07
[6 empty] | Sensor | 13.33%
[6 empty] | Logic | 13.17%
[6 empty] | Final element | 81.67%
Subsystem PFH Estimates
Rounding to | 2 | significant figures
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
[13 empty] | β for 1oo2 architecture |  | β for MooN architecture
Subsystem Index | PFH |  | FMEA sheet name | M | N | Voting | T1 years |  | MTTR days | MRT days | MTTR hours | MRT hours | β | βD | MooN β | MooN βD | λdu FITS | λdu per hour | λdd FITS | λdd per hour | DC | SFF |  | λd per hour | λsu FITS | λsu per hour |  | MDT1oo2 | CCF term | PFHDMooN | PFH
PZHH01 | 8e-08 |  | FMEA_1 | 1 | 3 | 1oo3 | 1 |  | 3 | 3 | 72 | 72 | 0.1 | 0.1 | 0.05 | 0.05 | 390 | 3.9e-07 | 1200 | 1.2e-06 | 75.47% | 80.98% |  | 1.59e-06 | 460 | 4.6e-07 | 6 | 0.0017315 | 7.95e-08 | 7.0159e-12 | 7.9507e-08
Solver1 | 7.9e-08 |  | FMEA_2 | 2 | 3 | 2oo3 | 1 |  | 3 | 3 | 72 | 72 | 0.05 | 0.05 | 0.075 | 0.075 | 50 | 5e-08 | 1000 | 1e-06 | 95.24% | 95.45% |  | 1.05e-06 | 50 | 5e-08 | 6 | 0.0002725 | 7.875e-08 | 8.1752e-11 | 7.8832e-08
FE01 | 4.9e-07 |  | FMEA_3 | 2 | 3 | 2oo3 | 1 |  | 3 | 3 | 72 | 72 | 0.1 | 0.1 | 0.15 | 0.15 | 2300 | 2.3e-06 | 140 | 1.4e-07 | 5.738% | 20.69% |  | 2.44e-06 | 460 | 4.6e-07 | 6 | 0.0087122 | 3.66e-07 | 1.2023e-07 | 4.8623e-07
Insert additional rows if needed above this row to maintain the range name references, and copy calculations into the new rows as required

## FMEA_1
Failure Mode Effects and Diagnostics Analysis |  |  |  | FOR EXAMPLE ONLY |  |  | Enter data only in the shaded cells |  |  |  |  | Use dropdown lists in the darker cells
Eqpt ID | PZHH01 | Eqpt Description | Pressure transmitter, trip on high level
|  | Manufacturers and models | Generic 4-20mA pressure transmitter with impulse line connection
|  | Reliability data sources used | Quote references sources here
|  | Evidence of suitability for use | Refer to either a safety manual or to a prior use analysis report
Type A/B: | Type B
[5 empty] | λ FITS |  | DCD | SFF | PTC | λD FITS | λDD FITS | λDU FITS | λDN FITS | λSD FITS | λSU FITS
Failure rates measured in FITS, failures per 109 hours |  |  |  | TOTALS: | 2600 |  | 75% | 85% | 97.18% | 1600 | 1200 | 390 | 11 | 550 | 460
Ref No | Component | Potential Failure Mode | Failure Effect(s) | Potential Causes | Expected freq λ FITS | Design controls and/or diagnostics | % Detectable by diagnostic | % Dangerous | % Revealed by periodic test and inspection | λD FITS | λDD FITS | λDU FITS | λDN FITS | λSD FITS | λSU FITS | Remarks
1 | Process connection | Blockage or clogging | Reduced sensitivity, delay, inability to sense high pressure causing low signal, spurious trip |  | 300 | Noise spectrum diagnostic | 90% | 100% | 100% | 300 | 270 | 30 | 0 | 0 | 0 | [EXAMPLE REMARKS ARE SHOWN HERE] Confirm that diagnostic is correctly configured
2 | Diaphragm | Corrosion | Corrosion can cause leakage, loss of pressure causing low signal, spurious trip |  | 30 | Periodic testing | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 30 | Confirm that calibration checks are included in annual test
3 | Electronics | Calibration drift | Drift causing higher signal causes spurious trip |  | 300 | Periodic testing | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 300 | Confirm that calibration checks are included in annual test Consider implementing sensor comparison
4 | Electronics | Calibration drift | Drift causing lower signal prevents trip |  | 150 | Periodic testing | 0% | 100% | 100% | 150 | 0 | 150 | 0 | 0 | 0 | Confirm that calibration checks are included in annual test
5 | Electronics | Noise or interference | Degraded signal may prevent trip |  | 300 | Data validation | 30% | 50% | 90% | 150 | 45 | 105 | 10.5 | 45 | 105 | Confirm if signal processing function block can detect noise Calibration check should detect degraded signal unless intermittent
6 | Electronics | Oscillation | Loss of signal |  | 30 | Data validation | 100% | 0% | 100% | 0 | 0 | 0 | 0 | 30 | 0 | Confirm if signal processing function block can detect oscillation Calibration check should detect degraded signal unless intermittent
7 | Electronics | Stuck in a fixed position |  |  | 100 | Data validation | 100% | 0% | 100% | 0 | 0 | 0 | 0 | 100 | 0 | Confirm if signal processing function block can detect stuck signal
8 | Wiring | Open circuit | Loss of signal |  | 100 | Data validation | 99% | 0% | 100% | 0 | 0 | 0 | 0 | 99 | 1
9 | Wiring | Short circuit | Loss of signal |  | 100 | Data validation | 100% | 0% | 100% | 0 | 0 | 0 | 0 | 100 | 0
10 | Wiring | High impedance | Degraded signal, reading low, prevents trip |  | 100 | Voltage/current characteristic diagnostic | 90% | 100% | 100% | 100 | 90 | 10 | 0 | 0 | 0 | Confirm that diagnostic is correctly configured
11 | Wiring | Low impedance | Degraded signal, reading high, causes spurious trip |  | 100 | Voltage/current characteristic diagnostic | 90% | 0% | 100% | 0 | 0 | 0 | 0 | 90 | 10 | Confirm that diagnostic is correctly configured
12 | Input channel | Other | Consolidated failure rates taken from PLC safety manual |  | 1000 | PLC diagnostics | 90% | 90% | 100% | 900 | 810 | 90 | 0 | 90 | 10
13 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
14 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
15 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
16 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
17 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
18 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
19 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
20 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
21 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
22 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
23 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
24 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
25 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
26 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
27 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
28 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
29 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
30 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Insert additional rows needed above this row to maintain the range name references

## FMEA_2
Failure Mode Effects and Diagnostics Analysis |  |  |  | FOR EXAMPLE ONLY |  |  | Enter data only in the shaded cells |  |  |  |  | Use dropdown lists in the darker cells
Eqpt ID | Solver1 | Eqpt Description | Logic solver
|  | Manufacturers and models | Generic 2oo3
|  | Reliability data sources used | Quote references sources here
|  | Evidence of suitability for use | Refer to either a safety manual or to a prior use analysis report
Type A/B: | Type B
[5 empty] | λ FITS |  | DCD | SFF | PTC | λD FITS | λDD FITS | λDU FITS | λDN FITS | λSD FITS | λSU FITS
Failure rates measured in FITS, failures per 109 hours |  |  |  | TOTALS: | 3100 |  | 90.91% | 98.39% | 100% | 1100 | 1000 | 50 | 0 | 2000 | 50
Ref No | Component | Potential Failure Mode | Failure Effect(s) | Potential Causes | Expected freq λ FITS | Design controls and/or diagnostics | % Detectable by diagnostic | % Dangerous | % Revealed by periodic test and inspection | λD FITS | λDD FITS | λDU FITS | λDN FITS | λSD FITS | λSU FITS | Remarks
0 | Consolidated failure rates taken from safety manual |  |  |  | 3100 |  |  |  |  | 1050 | 1000 | 50 | 0 | 2000 | 50 | [USE THIS ROW IF THE LOGIC SOLVER SAFETY MANUAL PROVIDES CONSOLIDATED FAILURE DATA]
1 | Main processor | Other | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [ALTERNATIVELY, FAILURE RATES MAY BE ESTIMATED BY ANALYSING EACH COMPONENT IN THE SYSTEM]
2 | Power supply | Other | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0
3 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
4 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
5 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
6 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
7 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
8 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
9 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
10 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
11 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
12 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
13 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
14 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
15 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Insert additional rows needed above this row to maintain the range name references

## FMEA_3
Failure Mode Effects and Diagnostics Analysis |  |  |  | FOR EXAMPLE ONLY |  |  | Enter data only in the shaded cells |  |  |  |  | Use dropdown lists in the darker cells
Eqpt ID | FE01 | Eqpt Description | Ball valve with solenoid controlled 1/4 turn pneumatic actuator, tight shutoff not required, clean service, spring to close, close on trip
|  | Manufacturers and models | Generic data
|  | Reliability data sources used | Quote references sources here
|  | Evidence of suitability for use | Refer to either a safety manual or to a prior use analysis report
Type A/B: | Type A
[5 empty] | λ FITS |  | DCD | SFF | PTC | λD FITS | λDD FITS | λDU FITS | λDN FITS | λSD FITS | λSU FITS
Failure rates measured in FITS, failures per 109 hours |  |  |  | TOTALS: | 3000 |  | 5.6% | 24.67% | 97.83% | 2500 | 140 | 2300 | 50 | 140 | 460
Ref No | Component | Potential Failure Mode | Failure Effect(s) | Potential Causes | Expected freq λ FITS | Design controls and/or diagnostics | % Detectable by diagnostic | % Dangerous | % Revealed by periodic test and inspection | λD FITS | λDD FITS | λDU FITS | λDN FITS | λSD FITS | λSU FITS | Remarks
1 | Solenoid valve | Stuck on | Ball valve fails to close on command |  | 300 |  | 0% | 100% | 100% | 300 | 0 | 300 | 0 | 0 | 0
2 | Solenoid valve | Stuck off | Ball valve fails to open on command |  | 10 |  | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 10
3 | Solenoid valve | Open circuit | Ball valve closes uncommanded | Overheated coil | 100 |  | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 100
4 | Actuator | Stuck on | Ball valve fails to close on command |  | 300 |  | 0% | 100% | 100% | 300 | 0 | 300 | 0 | 0 | 0
5 | Actuator | Stuck off | Ball valve fails to open on command |  | 30 |  | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 30
6 | Actuator | Deterioration | Ball valve closing time exceeds specification | Corrosion | 300 |  | 0% | 100% | 100% | 300 | 0 | 300 | 0 | 0 | 0
7 | Ball valve | Stuck on | Ball valve fails to close on command |  | 1000 |  | 0% | 100% | 100% | 1000 | 0 | 1000 | 0 | 0 | 0
8 | Ball valve | Stuck off | Ball valve fails to open on command |  | 100 |  | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 100
9 | Ball valve | Deterioration | Ball valve closing time exceeds specification |  | 300 |  | 0% | 100% | 100% | 300 | 0 | 300 | 0 | 0 | 0
10 | Ball valve | Other | Ball valve fails to close on command | Sheared stem due to over-torque | 100 |  | 0% | 100% | 50% | 100 | 0 | 100 | 50 | 0 | 0 | Include checks for sheared stem in proof test and inspection
11 | Wiring | Open circuit | Ball valve closes uncommanded |  | 100 |  | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 100
12 | Wiring | Short circuit | Ball valve closes uncommanded |  | 100 |  | 0% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 100
13 | Output channel | Other | Consolidated failure rates taken from PLC safety manual |  | 300 | PLC diagnostics | 90% | 50% | 100% | 150 | 135 | 15 | 0 | 135 | 15
14 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
15 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
16 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
17 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
18 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
19 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
20 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
21 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
22 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
23 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
24 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
25 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
26 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
27 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
28 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
29 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
30 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
Insert additional rows needed above this row to maintain the range name references

## Rate Converter
Use this sheet to convert failure rate units
Read the converted rates in this table
Enter data only in the shaded cells |  | Failure rate per hour | Failure rate per 106 hours | FITS (Failure rate per 109 hours) | Failure rate per year | Mean time to or between failure, in years
Failure rate per hour | 1e-06 | 1e-06 | 1 | 1000 | 0.00876 | 114.1553
Failure rate per 106 hours | 1 | 1e-06 | 1 | 1000 | 0.00876 | 114.1553
FITS (Failure rate per 109 hours) | 1000 | 1e-06 | 1 | 1000 | 0.00876 | 114.1553
Failure rate per year | 0.01 | 1.1416e-06 | 1.1416 | 1141.5525 | 0.01 | 100
Mean time to or between failure, in years | 100 | 1.1416e-06 | 1.1416 | 1141.5525 | 0.01 | 100

## MooN table (hidden)
β multiplier | N | [6 empty] | HFT corresponding to MooN architectures | [6 empty] | Examples to illustrate STR β multiplier selection
M | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | PFD | STR |  | multiplier | row | col | STR N-M+1 | STR N
1 |  | 1 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 3oo3 | 1oo3 | tolerates 0 faults with 3 chances | 0 | 3 | 3 | 3 | 3
2 |  |  | 1.5 | 0.6 | 0.4 | 0.4 | 0.4 |  | 0 | 1 | 2 | 3 | 4 | 5 | 1oo3 | 3oo3 | tolerates 2 faults with 3 chances | 0.5 | 1 | 3 | 1 | 3
3 |  |  |  | 1.75 | 0.8 | 0.8 | 0.8 |  |  | 0 | 1 | 2 | 3 | 4 | 2oo3 | 2oo3 | tolerates 1 fault with 3 chances | 1.5 | 2 | 3 | 2 | 3
4 |  |  |  |  | 2 | 2 | 2 |  |  |  | 0 | 1 | 2 | 3 | 1oo4 | 4oo4 | tolerates 3 faults with 4 chances | 0.3 | 1 | 4 | 1 | 4
5 | [5 empty] | 3 | 3 |  | 4 3: 0; 5 4: 1; 6 5: 2
6 | [6 empty] | 4 |  | 5 4: 0; 6 5: 1 | The rows in the β multiplier table correspond to the number of channels that are required to operate correctly for the
7 | [8 empty] | 6 5: 0 | function to act as specified. The columns correspond to N, the total number of channels.
From IEC 61058-6 | [8 empty] | 1 0: For PFD, MooN can tolerate N-M faults
Extended as per Dr David J Smith ‘Reliability, Maintainability and Risk’, 9th Ed. Butterworth Heinemann. 2017 | [14 empty] | A MooN architecture needs a minimum of M channels in the trip state to trip successfully on demand. The β
scaling factor used for PFD calculations is taken from the Mth row and the Nth column
A MooN architecture will trip spuriously if at least M channels have undetected safe failures putting them into
ST multiplier | N | [13 empty] | the trip state. The remaining N-M channels might be in a normal healthy state or they might have dangerous
M | 1 | 2 | 3 | 4 | 5 | 6 | 7 | [7 empty] | faults that prevent trip. N-M+1 channels are required to be in the non-trip state to avoid spurious trip.
1 |  | 0.8333 | 0.6667 | 0.5229 | 0.4053 | 0.3117 | 0.2383 | [7 empty] | The β scaling factor used in estimating the overall spurious trip rate is therefore taken from the
2 |  |  | 0.8889 | 0.75 | 0.6144 | 0.4938 | 0.3917 | [7 empty] | (N-M+1)th row and the Nth column.
3 |  |  |  | 0.9167 | 0.8 | 0.6765 | 0.5598
4 |  |  |  |  | 0.9333 | 0.8333 | 0.7215
5 | [5 empty] | 0.9444 | 0.8571
6 | [6 empty] | 0.9524
7
SINTEF 2013
β multiplier | N
M | 1 | 2 | 3 | 4 | 5 | 6
1 |  | 1 | 0.5 | 0.3 | 0.21 | 0.17
2 |  |  | 2 | 1.1 | 0.7 | 0.4
3 |  |  |  | 2.9 | 1.8 | 1.1
4 |  |  |  |  | 3.7 | 2.4
5 | [5 empty] | 4.3

## Lookup tables (hidden)
Failure Modes | Frequency | FITS | pa | MTTF, y | Ranking | Detectability | Dangerous fraction | Type selection | 61508-2 Table 2: TYPE A | [7 empty] | 61511 |  | RRF | SIL | HFT Routes |  | Uncertainty range mulitpliers |  | βint
Stuck on | Remote, unlikely | 1 | 8.76e-06 | 110000 | 1 | 100% | 100% | Type A | [14 empty] | orders of magnitude
Stuck off | Very low | 10 | 8.76e-05 | 11000 | 2 | 99% | 90% | Type B | SFF | 0 | 1 | 2 | 3 | 4 | 5 | 6 | HFT | SIL | 1 | 0 | Route 1H | 1 | 1 | 3.16 | 0.5%
Stuck in a fixed position | Low | 30 | 0.0002628 | 3800 | 3 | 90% | 50% |  | 0% | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 0 | 2 | 10 | 1 | Route 2H | 2 | 2 | 10 | 1%
Open circuit | Moderate, occasional | 100 | 0.000876 | 1100 | 4 | 50% | 30% |  | 60% | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 1 | 3 | 100 | 2 | IEC 61511 | 3 | 3 | 31.6 | 2%
Short circuit | Moderate | 300 | 0.002628 | 380 | 5 | 30% | 10% |  | 90% | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 4 | 1000 | 3 | TBA | 4 |  |  | 5%
High impedance | High | 1000 | 0.00876 | 110 | 6 | 10% | 3% |  | 99% | 3 | 4 | 4 | 4 | 4 | 4 | 4 |  |  | 10000 | 4 |  |  |  |  | 10%
Low impedance | Very high, repeated | 3000 | 0.02628 | 38 | 7 | 0% | 1%
Calibration drift | Very high, inevitable | 10000 | 0.0876 | 11 | 8 |  | 0% | [11 empty] | PFH | SIL | Suitability: |  | SC |  | True/False
Oscillation | [8 empty] | 61508-2 Table 3: TYPE B
Noise or interference | [18 empty] | 1e-09 | 4 | IEC 61511 prior use dossier |  | 0 |  | TRUE
Contamination | Rounding to | 2 | significant figures | [15 empty] | 1e-08 | 3 | IEC 61508 safety manual |  | 1 |  | FALSE
Deterioration | [8 empty] | SFF | 0 | 1 | 2 | 3 | 4 | 5 | 6 |  |  | 1e-07 | 2 | Other safety manual |  | 2
Blockage or clogging | [8 empty] | 0% | 0 | 1 | 2 | 3 | 4 | 4 | 4 |  |  | 1e-06 | 1 | Evidence not available |  | 3
Corrosion | [8 empty] | 60% | 1 | 2 | 3 | 4 | 4 | 4 | 4 |  |  | 1e-05 | 0 |  |  | 4
Vibration | [8 empty] | 90% | 2 | 3 | 4 | 4 | 4 | 4 | 4
Degraded power supply | [8 empty] | 99% | 3 | 4 | 4 | 4 | 4 | 4 | 4
Failure of diagnostics
Operates prematurely
Rupture
Other
Failure mode = event that causes functional failure
Failure effect = what happens when a failure mode occurs